## Slide 1
PREDICTIVE COOLING MAINTENANCE
Knowing which part is failing, four hours early
A digital twin for the server room that predicts CRAC equipment failure, identifies the mechanism, and recommends the right intervention while the fault is still developing.
Investment case · Security · Ethical safety
Team members
Lourduraj John Charles (1011136) · Yang Xingyu (1010962)
Syed Adeel Ahmed Mustaq Ahamed (1011010) · Kuhu Gupta (1010814)
Submission date: 16 August 2026
Notes: Frame: this is a maintenance decision-support system, not a thermostat. The pitch covers business value, security and ethical safety.

## Slide 2
By the time the room is hot, it is already late
A cooling fault shows in equipment behaviour long before it shows in temperature
HOURS BEFORE
Motor current rises.
Filter pressure climbs.
Vibration increases.
Invisible to a thermostat
MINUTES BEFORE
Airflow drops.
Supply air warms.
Rack inlets creep up.
Still below alarm threshold
THE ALARM
Threshold crossed.
Servers throttling.
Emergency callout.
Response begins here today
Raising cooling output is not always the right answer. Temperature rises from workload, from poor airflow, or from equipment degradation — and each needs a different response.
Notes: The core problem is not detection speed alone — it is that a temperature reading cannot tell you what to do about it.

## Slide 3
What the system does
Four coordinated twins over the existing telemetry link
01
Predicts
Equipment failure up to four hours ahead, with a time-to-failure countdown.
02
Identifies
Which mechanism is failing — worn fan bearing or clogged filter.
03
Explains
The sensor evidence behind every warning, and which model raised it.
04
Recommends
The proportionate action, with the evidence behind it. Never acts alone.
Operator approval is required for every action. Nothing in the system actuates equipment.
Notes: Four twins: racks, cooling, occupancy/workload, energy. Coordinated centrally because they share one thermal zone.

## Slide 4
A threshold tells you it is hot. It cannot tell you why.
This is the difference no alarm setting can close
TEMPERATURE THRESHOLD
“CRAC-01 is running hot.”
One undifferentiated callout
Technician diagnoses on arrival
Wrong guess closes the ticket
THIS SYSTEM
“Filter clogging. Replace filter.”
Names the failing mechanism
Different part, different job, different urgency
Mechanism named from which sensor limits tripped
Getting this wrong is worse than not knowing. A technician replaces a clean filter, closes the ticket, and the bearing keeps degrading — with the alarm already acknowledged and the lead time spent.
Notes: Lead this argument. It is categorical — no threshold at any alarm level can identify a mechanism.

## Slide 5
And it sees the fault sooner
Median warning before failure, across 31 failing test runs
1.5×
more warning time
MEASURED CONSERVATIVELY
This system
292.5 min
Best conventional threshold
195.2 min
The baseline is computed from the same test runs using the same lead-time function — not a fixed number chosen to flatter the result. Both detectors caught all 31 failing runs.
Almost five hours of warning — enough to schedule maintenance rather than react to an outage.
Notes: 2.1x is the defensible floor. Earlier baselines fire later and would give a larger multiple; we chose the strongest available comparison.

## Slide 6
Where the value comes from
Illustrative annual benefit per monitored CRAC unit
SGD 24,000
per CRAC, per year
MEASURED
0.993 AUC, 0.925 F1, 0.08 false alarms per healthy run.
ASSUMED
Every figure on this slide is a planning assumption.
Avoided downtime
12,000
Cooling energy
6,000
Avoided callout premium
4,000
Reduced manual monitoring
2,000
Avoided cost depends on how long a fault would otherwise run undetected — an interval this project cannot measure. The pilot phase measures it directly and replaces this assumption.
Notes: Be first to name the weak assumption. 4,000 SGD avoided failure is 58% of benefit and rests on a failure interval this project cannot measure.

## Slide 7
Return on investment
Base case, and the same case with every benefit halved
BASE CASE
BENEFITS HALVED
Payback on capital
7.6 months
16.8 months
Year 1 return
50 %
does not recover
Three-year return
260 %
80 %
The first year is not guaranteed
If benefits are half what we assume, year 1 does not recover its own cost and payback stretches to 16.8 months.
The case still holds
Over three years the halved case still returns 80%. Integration cost is one-off, so each additional unit is far cheaper than the first.
Notes: The sensitivity case changes the recommendation rather than decorating it: fund Phase 2 as validation, commit capital at Phase 3.

## Slide 8
Security
A system that advises engineers must protect the integrity of its advice
Authenticated clients
Per-service credentials. Anonymous connections refused.
Least privilege
Topic permissions per identity. One identity only may publish a recommendation.
Encrypted transport
TLS for all broker connections in deployment.
Liveness detection
Every twin publishes a retained offline marker if it drops. Implemented and verified.
THE THREAT THAT MATTERS MOST
A forged maintenance recommendation is a fabricated instruction to an engineer.
That turns the system into an attack channel against staff — worse than any data loss it could suffer.
So exactly one identity may write one, and every recommendation is recorded with its source.
Notes: Security was implemented and then tested by attempting the attacks it should prevent. Three real defects surfaced in the process and were fixed.

## Slide 9
Ethical safety
The limitation we can name, and how we manage it
WHAT WE FOUND
The model is trained on two failure mechanisms. Against a third — a refrigerant leak, a failing compressor — it has no basis for recognition. It would stay confident about what it knows and quiet about what it does not.
Its failure mode is silence, not error.
HOW WE MANAGE IT
Autonomy is bounded and comes last, so the model’s silence cannot cause an action. The mitigation for wider deployment is a second, simpler model on raw sensor values running alongside the primary one, escalating when either fires – buying coverage on unfamiliar faults at the cost of precision on familiar ones.
Stated as a limitation, not designed around.
Human oversight
Advisory only. No autonomous control anywhere in the system.
Transparency
Every alert carries its sensor evidence, its confidence, and the mechanism.
Stated limits
Performance figures come from simulation and are an upper bound, not a forecast.
Notes: The strongest ethics claim is not that there are no weaknesses — it is that we measured one and mitigated it at a stated cost.

## Slide 10
From prototype to deployment
Each phase buys the answer the next one needs
1
Prototype
Simulated room, four twins, hardened broker
COMPLETE
2
Live pilot
One CRAC, physical sensors, shadow mode
NOT STARTED
3
Full room
Four CRACs, maintenance-system integration
NOT STARTED
4
Multi-room
Three rooms, twelve CRACs, federation layer
NOT STARTED
5
Bounded autonomy
Setpoint ±1 °C and workload shift only
NOT STARTED
Autonomy comes last by evidence, not caution — automatic action is limited to changes whose worst outcome is a slightly warmer room.
Notes: Phase 2 exists to test the assumption most likely to fail: that the model survives real sensor noise.

## Slide 11
What would change this recommendation
A business case that lists only upside is not a business case
Real sensors are noisier
Our figures come from a simulator. Trend features are the most flattered by clean data, and they carry the predictive advantage.
The failure interval is wrong
Avoided downtime is half the benefit and rests on an interval no data here supports.
Faults are caught anyway
If existing maintenance already catches these faults early, the energy benefit shrinks sharply.
THE ASK
Fund the live pilot as a validation exercise — one CRAC unit in shadow mode, to learn whether the model survives real sensors before wider capital is committed.
Notes: Close on the ask, framed honestly: Phase 2 buys information, not return. The return case begins at Phase 3.