PROJECT 2 — GOVERNANCE, ETHICS AND STRATEGIC ROADMAP

Intelligent Data Center
Digital Twin Ecosystem

Cybersecurity · ROI Analysis · Algorithmic Transparency · Bias Mitigation · Deployment Roadmap

This document addresses two Key Tasks: Governance & Ethics (Part A) and Strategic Roadmap (Part B). Financial figures are illustrative assumptions for planning purposes and are labelled as such throughout. Measured system results are labelled MEASURED and are reproducible from the committed notebook.

# Contents

| § | Section | Covers |
| --- | --- | --- |
| A1 | Threat model | What an attacker could do to a decision-support twin |
| A2 | Cybersecurity measures | Controls, implementation status, verification method |
| A3 | Algorithmic transparency | What the system exposes per prediction |
| A4 | Bias mitigation | Distributional limits and how they are managed |
| A5 | Human oversight | Why nothing actuates automatically |
| B1 | ROI analysis | Benefits, costs, payback, sensitivity |
| B2 | Deployment roadmap | Five phases from prototype to bounded autonomy |
| B3 | Risks to the business case | What would change the recommendation |

# Part A — Governance and Ethics

## A1. Threat model

The system is decision support: it tells a human what is failing and what to do about it. Its security value therefore rests on the integrity of the advice, not only on the confidentiality of the data. The threats below are ordered by consequence.

| Threat | How it would work | Consequence |
| --- | --- | --- |
| Forged recommendation | An attacker publishes to the recommendation topic | A fabricated maintenance instruction reaches an engineer. Highest-consequence threat: it converts the system into an attack channel against staff. |
| Spoofed telemetry | False sensor readings published to a rack or CRAC topic | The model predicts on fiction. Either a fabricated alarm wasting a callout, or masking a genuine developing fault. |
| Suppressed telemetry | An attacker withholds or blocks publication | The twin goes stale silently. Mitigated by last-will-and-testament liveness on every twin. |
| Eavesdropping | Reading unencrypted broker traffic | Reveals occupancy patterns and facility load profile — useful reconnaissance for physical intrusion. |
| Model as attack surface | Crafted inputs pushed into the feature window | Predictions driven outside the training distribution. This is not hypothetical: an unrelated cadence defect produced exactly this effect and was corrected. |

## A2. Cybersecurity measures

Controls are listed with their implementation status stated plainly. The prototype runs on a local trusted broker; controls marked as specified are designed and documented but are deployment requirements rather than prototype features.

| Control | Detail | Status |
| --- | --- | --- |
| Authenticated clients | Per-service credentials — simulator, each twin, orchestrator, dashboard. Anonymous connections refused. | Specified for deployment |
| Topic access control | Least privilege per identity. Exactly one identity may publish to the recommendation topic. | Specified for deployment |
| Encrypted transport | TLS for all broker connections; the prototype broker also exposes a plaintext listener for local development only. | Specified for deployment |
| Liveness detection | MQTT last-will-and-testament: every twin publishes a retained offline marker if its connection drops. | Implemented and verified |
| Input validation | Timestamp validity, rejection of unknown asset identifiers, schema enforcement at the twin boundary. | Partially implemented |
| Audit trail | Append-only record of predictions, recommendations and operator acknowledgements, sequenced per source. | Specified for deployment |
| Network segmentation | The twin network is isolated from any building-control network. No path exists from the twin to plant equipment. | Architectural — enforced by design |

Verification principle: a security control is only credible if the attack it prevents has been attempted. Controls should be tested by attempting an unauthenticated publish and by attempting to publish a forged recommendation from an authenticated but unprivileged identity, with the broker responses recorded.

## A3. Algorithmic transparency

An operator asked to schedule maintenance on the strength of a model output must be able to see why. Every prediction carries its own explanation.

| Exposed with every prediction | Purpose |
| --- | --- |
| Failure probability | The model's confidence, shown as a number rather than a binary alarm |
| Time to failure | Published only above the action threshold, where the regressor has training support. Below it, no countdown is shown rather than an extrapolated one. |
| Contributing factors | The sensor evidence behind the prediction, so the operator can sanity-check it against the equipment |
| Predicted failure mode | Which mechanism is degrading — this determines the action, not merely its urgency |
| Threshold flags | The plain rule state alongside the model output, so the two can be compared directly |

Both models are interpretable by construction. A tree ensemble supports per-prediction feature attribution, and the linear time-to-failure regressor can be read as coefficients. Neither is a black box in the sense that would prevent an engineer from auditing a decision.

The system also states what it does not know. Performance figures come from a simulator, and the documentation records this as an upper bound rather than a field estimate.

## A4. Bias mitigation

In this system, bias is distributional rather than demographic. The relevant question is not fairness between people but whether the model performs evenly across the conditions it will meet.

| Source of bias | Treatment |
| --- | --- |
| Class imbalance | Failure states are rare by construction. Accuracy is not reported; precision, recall and F1 are, with the operating threshold stated. |
| Temporal leakage | Train and test are split on run identifier, never on rows. Consecutive samples within a run are near-identical, and a row split would inflate every score. |
| Ground-truth leakage | Simulator internal state variables are excluded from the feature set. Only quantities a real sensor could measure are used. |
| Per-asset variation | Training data spans all racks and all load levels so no single asset dominates the fitted model. |
| Unseen failure mechanisms | The model is trained on two mechanisms. Its behaviour on a third is unknown, and it should be assumed to under-detect rather than to generalise. |

The most important limitation is the last one. A model trained on bearing wear and filter clogging has no basis for recognising a mechanism it has never seen — a refrigerant leak, a failing compressor, a control-board fault. It will remain confident about what it recognises and quiet about what it does not. Recommended mitigation: retain a simpler model trained on raw sensor values alongside the primary model, and escalate when either fires. This trades precision on known mechanisms for coverage on unknown ones, and the trade should be stated rather than hidden.

Recommended verification: train on one failure mechanism and test on the other, in both directions. Report recall separately from AUC — ranking can transfer while a fixed decision threshold does not, and it is the threshold that determines whether an operator is warned.

## A5. Human oversight and error cost

| Principle | Implementation |
| --- | --- |
| Advisory only | No component actuates equipment. Every action is a recommendation requiring operator approval. |
| False positive cost | An unnecessary inspection or filter change. Cost is bounded and financial. |
| False negative cost | Hardware damage and possible service loss. Cost is unbounded. |
| Chosen asymmetry | Recall is prioritised over precision because the costs are asymmetric. This is a deliberate choice and is stated rather than implied. |
| Alarm fatigue | Escalation requires sustained high risk rather than a single sample, so a transient spike does not raise a critical alert. |
| Load-versus-fault separation | Alerts explained by high occupancy with no equipment threshold tripped are suppressed, so operators are not called out for demand-driven heat. |

# Part B — Strategic Roadmap

## B1. ROI analysis

Every financial figure in this section is an illustrative planning assumption, not measured operating data. They are stated so the reasoning can be checked and the inputs replaced with site data once available.

Benefits are expressed per monitored CRAC unit per year.

| Benefit stream | SGD / year | Basis |
| --- | --- | --- |
| Avoided unplanned downtime | 12,000 | Failures predicted early enough to remediate in a scheduled window |
| Avoided emergency maintenance premium | 4,000 | Difference between planned and callout labour rates |
| Cooling energy savings | 6,000 | Occupancy-aware setpoint relaxation and earlier correction of degraded operation |
| Reduced manual monitoring | 2,000 | Automated trend surveillance replacing periodic manual checks |
| Gross annual benefit | 24,000 |  |

Costs separate one-off capital from recurring operating expenditure.

| Cost item | SGD | Type |
| --- | --- | --- |
| Sensors and gateway | 4,000 | Capital |
| Software and infrastructure | 3,000 | Capital |
| Integration and model development | 7,000 | Capital |
| Total capital | 14,000 |  |
| Maintenance and support | 2,000 | Recurring, annual |
| Total first-year cost | 16,000 |  |

## B1.1 Returns

Payback is measured against capital only. Including recurring operating cost in a payback figure conflates a one-off outlay with an ongoing obligation and overstates the recovery period.

| Measure | Calculation |
| --- | --- |
| Year 1 ROI | (24,000 − 16,000) ÷ 16,000 = 50 % |
| Net annual benefit | 24,000 − 2,000 recurring = 22,000 |
| Net monthly benefit | 22,000 ÷ 12 = 1,833 |
| Payback on capital | 14,000 ÷ 1,833 = 7.6 months |
| Three-year ROI | (72,000 − 20,000) ÷ 20,000 = 260 % |

## B1.2 Sensitivity

The single largest assumption is avoided downtime, which is half the gross benefit and rests on a failure interval this project cannot measure. If every benefit is half what is assumed:

| Measure | Halved-benefit case |
| --- | --- |
| Gross annual benefit | 12,000 |
| Net annual benefit | 10,000 |
| Payback on capital | 16.8 months |
| Year 1 ROI | negative — the first year does not recover its own cost |
| Three-year ROI | (36,000 − 20,000) ÷ 20,000 = 80 % |

The project still returns over a three-year horizon in the halved case, but not within the first year. Presenting only the base case would misrepresent that. The pilot phase exists specifically to replace the assumed downtime interval with a measured one before larger capital is committed.

## B2. Deployment roadmap

Each phase is scoped to answer the question the next phase depends on, so that capital is committed only after the preceding uncertainty is resolved.

| # | Phase | Scope | What it establishes |
| --- | --- | --- | --- |
| 1 | Prototype | Simulated room, six twins, central orchestration, predictive model, dashboard | That the method works end to end. It establishes nothing about a physical CRAC unit. |
| 2 | Live pilot | One production CRAC, physical sensors, shadow mode — predictions recorded, not acted on | Whether the model survives real sensor noise, and what the true undetected-fault interval is. This replaces the largest assumption in the ROI model. |
| 3 | Full server room | All CRAC units, integration with the maintenance management system | Whether the advice changes what maintenance actually does. Per-unit capital falls sharply here as integration cost is already sunk. |
| 4 | Multi-room | Several rooms, federation layer between room-level twins | That centralized-within-zone and federated-across-zones is the correct split at scale. |
| 5 | Bounded autonomy | Automatic execution limited to setpoint adjustment within ±1 °C and workload redistribution | That autonomy can be narrow without being general. Restricted to actions whose worst outcome is a slightly warmer room. |

Autonomy is last for a measured reason, not from caution. A model that under-detects unfamiliar failure mechanisms should not be given control authority, because its failure mode is silence rather than error. Automatic action is therefore confined to changes that are safe even when the model is wrong.

## B3. Risks to the business case

A business case that lists only upside is not a business case. These are the conditions under which the recommendation should change.

| Risk | Effect and mitigation |
| --- | --- |
| Real sensors are noisier than simulated ones | All performance figures derive from a simulator whose noise model is optimistic. Trend features are the most flattered by clean data and are also the ones carrying the predictive advantage. Phase 2 exists to test exactly this. |
| The assumed failure interval is wrong | Avoided downtime is half the gross benefit and rests on an interval no data here supports. Phase 2 measures it directly in shadow mode. |
| Existing maintenance already catches these faults | If planned maintenance already intercepts most degradation, the avoided-downtime benefit shrinks sharply and the case rests on energy savings alone. |
| A novel failure mechanism appears | The model would under-detect it. Mitigated by the dual-model escalation rule in section A4, at a cost in precision. |
| Operators stop trusting the alerts | Suppression of load-driven alerts and sustained-risk escalation are both aimed at this. If the false alarm rate rises in production, adoption fails regardless of accuracy. |
| Scope expands during deployment | Phase boundaries are defined by the question each answers. A phase that grows beyond its question should be split rather than extended. |